## Pressures 1000-13FF
FIELDBUS REGISTER TABLE ecc 4.0
Register Name | Write access by Sauer | Read access by Sauer | Write access by customer | Read access by customer | Register Start | Register Stop | Max. Register Lenght | Register Adress | Register Lenght | Data Conversion Type | Data Conversion Type reserve | Note | Name
Feed pressure (pressure receiver (supplied by customer)) | N | J | N | J | 1000 | 1001 | 2 | 1000 | 2 | uns_16 | uns_32 | Reads 98 | PT002
Raw value | N | J | N | J | 1002 | 1003 | 2 | 1002 | 2 | uns_16 | uns_32 | No reply
Start pressure | J | J | J | J | 1004 | 1005 | 2 | 1004 | 2 | uns_16 | uns_32 | Reads 1
Stop pressure | J | J | J | J | 1006 | 1007 | 2 | 1006 | 2 | uns_16 | uns_32 | Reads 0
Error level | N | J | N | J | 100C | 100C | 1 | 100C | 1 | uns_8 | uns_16 | Reads 0
Suction pressure (after valve (compressor intake)) | N | J | N | J | 1012 | 1013 | 2 | 1012 | 2 | uns_16 | uns_32 | Reads 99 | PT003
Start pressure | J | J | J | J | 1016 | 1017 | 2 | 1016 | 2 | uns_16 | uns_32 | Reads 700
Stop pressure | J | J | J | J | 1018 | 1019 | 2 | 1018 | 2 | uns_16 | uns_32 | Reads 400
Error level | N | J | N | J | 1022 | 1022 | 1 | 1022 | 1 | uns_8 | uns_16 | Reads 0
Stage 1 pressure | N | J | N | J | 1028 | 1029 | 2 | 1028 | 2 | uns_16 | uns_32 | Reads 160 when running (0.01 atm) | PT110
Error level | N | J | N | J | 1030 | 1030 | 1 | 1030 | 1 | uns_8 | uns_16 | Reads 0
Stage 2 pressure | N | J | N | J | 1036 | 1037 | 2 | 1036 | 2 | uns_16 | uns_32 | Reads 716 when running (0.01 atm) | PT210
Error level | N | J | N | J | 103E | 103E | 1 | 103E | 1 | uns_8 | uns_16 | Reads 0
Stage 3 pressure | N | J | N | J | 1044 | 1045 | 2 | 1044 | 2 | uns_16 | uns_32 | Reads 2672 when running (0.01 atm) | PT310
Error level | N | J | N | J | 104C | 104C | 1 | 104C | 1 | uns_8 | uns_16 | Reads 0
Stage 4 pressure | N | J | N | J | 1052 | 1053 | 2 | 1052 | 2 | uns_16 | uns_32 | Reads 7952 when running (0.01 atm) | PT410
Error level | N | J | N | J | 105A | 105A | 1 | 105A | 1 | uns_8 | uns_16 | Reads 0
Stage 5 pressure | N | J | N | J | 1060 | 1061 | 2 | 1060 | 2 | uns_16 | uns_32 | Reads 7937 when running (0.01 atm) | PT510
Error level | N | J | N | J | 1068 | 1068 | 1 | 1068 | 1 | uns_8 | uns_16 | Reads 0
Stage 6 pressure | N | J | N | J | 106E | 106F | 2 | 106E | 2 | uns_16 | uns_32 | No reply
Error level | N | J | N | J | 1076 | 1076 | 1 | 1076 | 1 | uns_8 | uns_16 | No reply
System pressure | N | J | N | J | 107C | 107D | 2 | 107C | 2 | uns_16 | uns_32 | Reads 7808 when running (0.01 atm) | PT709
Start pressure | J | J | J | J | 1080 | 1081 | 2 | 1080 | 2 | uns_16 | uns_32 | Reads 20000 when running (0.01 atm)
Stop pressure | J | J | J | J | 1082 | 1083 | 2 | 1082 | 2 | uns_16 | uns_32 | Reads 25000 when running (0.01 atm)
Error level | N | J | N | J | 108C | 108C | 1 | 108C | 1 | uns_8 | uns_16 | Reads 0
Final pressure | N | J | N | J | 1092 | 1093 | 2 | 1092 | 2 | uns_16 | uns_32 | No reply
Error level | N | J | N | J | 109A | 109A | 1 | 109A | 1 | uns_8 | uns_16 | No reply
Cooling water inlet pressure | N | J | N | J | 10A0 | 10A1 | 2 | 10A0 | 2 | uns_16 | uns_32 | Reads 0
Error level | N | J | N | J | 10AC | 10AC | 1 | 10AC | 1 | uns_8 | uns_16 | Reads 0
Cooling water outlet pressure | N | J | N | J | 10B2 | 10B3 | 2 | 10B2 | 2 | uns_16 | uns_32 | Reads 0
Error level | N | J | N | J | 10BE | 10BE | 1 | 10BE | 1 | uns_8 | uns_16 | Reads 0
Cooling water differential pressure | N | J | N | J | 10C4 | 10C5 | 2 | 10C4 | 2 | uns_16 | uns_32 | Reads 0
Error level | N | J | N | J | 10CC | 10CC | 1 | 10CC | 1 | uns_8 | uns_16 | Reads 0
Oil pressure | N | J | N | J | 10D2 | 10D3 | 2 | 10D2 | 2 | uns_16 | uns_32 | Reads 272 | PT800
Error level | N | J | N | J | 10DC | 10DC | 1 | 10DC | 1 | uns_8 | uns_16 | No reply
Absolute pressure | N | J | N | J | 10E2 | 10E3 | 2 | 10E2 | 2 | uns_16 | uns_32 | Reads 0
Error level | N | J | N | J | 10EA | 10EA | 1 | 10EA | 1 | uns_8 | uns_16 | Reads 0
Crankcase pressure | N | J | N | J | 10F0 | 10F1 | 2 | 10F0 | 2 | uns_16 | uns_32 | Reads 0
Error level | N | J | N | J | 10F8 | 10F8 | 1 | 10F8 | 1 | uns_8 | uns_16 | Reads 0
Example:
| Modbus Addr.: 01 Get: 03 Set: 10 Start Register Register Length |  | Example:
Modbus Addr.: 01 Get: 03 Set: 10 Start Register Register Length
01 03 1004 0002 Get Start Pressure
| 01 10 1080 0002 04 0000 6590 Set Load Pressure |  | 01 03 1004 0002 Get Start Pressure
01 10 1080 0002 04 0000 6590 Set Load Pressure
6590(H)= 26000mbar 7530(H)= 30000mbar 04: Register Legth (witten)
6590(H)= 26000mbar 7530(H)= 30000mbar 04: Register Legth (witten)

## Temperatures 1400-17FF
Data conversion type is the actual memory required, data conversion type reserve is the memory to be reserved for this variable
Register name | Write access by Sauer | Read access by Sauer | Write access by customer | Read access by customer | Register Start | Register Stop | Max. Register Lenght | Register Adress | Register Lenght | Data Conversion Type | Data Conversion Type reserve | Offset | Note | Name
Outlet temperature | N | J | N | J | 1400 | 1401 | 2 | 1400 | 2 | int_16 | int_32 | 0 | in 0.01 C | TT519
Raw value | N | J | N | J | 1402 | 1403 | 2 | 1402 | 2 | int_16 | int_32 | 1 | No answer
Start block temperature (except 45xx, 6000) | J | J | J | J | 1404 | 1405 | 2 | 1404 | 2 | int_16 | int_32 | 2 | Returns 500
Error level | N | J | N | J | 140A | 140A | 1 | 140A | 1 | uns_8 | uns_16 | 5
Cooling water inlet temperature | N | J | N | J | 1410 | 1411 | 2 | 1410 | 2 | int_16 | int_32 | 8 | Returns 0
Error level | N | J | N | J | 141C | 141C | 1 | 141C | 1 | uns_8 | uns_16 | 14
Cooling water outlet temperature | N | J | N | J | 1422 | 1423 | 2 | 1422 | 2 | int_16 | int_32 | 17 | Returns 0
Error level | N | J | N | J | 142A | 142A | 1 | 142A | 1 | uns_8 | uns_16 | 21
Ambient temperature | N | J | N | J | 1430 | 1431 | 2 | 1430 | 2 | int_16 | int_32 | 24 | Returns 0
Error level | N | J | N | J | 1438 | 1438 | 1 | 1438 | 1 | uns_8 | uns_16 | 28 | Returns 0
Oil temperature | N | J | N | N ??? | 143E | 143F | 2 | 143E | 2 | int_16 | int_32 | 31 | Returns 0
Start block temperature | J | J | J | J | 1442 | 1443 | 2 | 1440 | 2 | int_16 | int_32 | 32 | Returns 0
Oil inlet temperature | N | J | N | N ??? | 1452 | 1453 | 2 | 1452 | 2 | int_16 | int_32 | 41 | Returns 0
Oil return temperature | N | J | N | N ??? | 1460 | 1461 | 2 | 1460 | 2 | int_16 | int_32 | 48 | Returns 0
Feed pressure temperature | N | J | N | J | 146E | 146F | 2 | 146E | 2 | int_16 | int_32 | 55 | Returns 0
Error level | N | J | N | J | 1476 | 1476 | 1 | 1476 | 1 | uns_8 | uns_16 | 59 | Returns 0
Motor temperature | N | J | N | J | 147C | 147D | 2 | 147C | 2 | int_16 | int_32 | 62 | Returns 0
Error level | N | J | N | J | 1484 | 1484 | 1 | 1484 | 1 | uns_8 | uns_16 | 66 | Returns 0
Motor phase 1 temperature | N | J | N | J | 148A | 148B | 2 | 148A | 2 | int_16 | int_32 | 69 | Returns 0
Error level | N | J | N | J | 1492 | 1492 | 1 | 1492 | 1 | uns_8 | uns_16 | 73 | Returns 0
Motor phase 2 temperature | N | J | N | J | 1498 | 1499 | 2 | 1498 | 2 | int_16 | int_32 | 76 | Returns 0
Error level | N | J | N | J | 14A0 | 14A0 | 1 | 14A0 | 1 | uns_8 | uns_16 | 80 | Returns 0
Motor phase 3 temperature | N | J | N | J | 14A6 | 14A7 | 2 | 14A6 | 2 | int_16 | int_32 | 83 | Returns 0
Error level | N | J | N | J | 14AE | 14AE | 1 | 14AE | 1 | uns_8 | uns_16 | 87 | Returns 0
Temperature sensor before stage 1.1 cooler | N | J | N | J | 14B4 | 14B5 | 2 | 14B4 | 2 | int_16 | int_32 | 90 | Reads about 15000 | TT111
Error level | N | J | N | J | 14BC | 14BC | 1 | 14BC | 1 | uns_8 | uns_16 | 94
Temperature sensor before stage 1.2 cooler | N | J | N | J | 14C2 | 14C3 | 2 | 14C2 | 2 | int_16 | int_32 | 97 | Returns 0
Error level | N | J | N | J | 14CA | 14CA | 1 | 14CA | 1 | uns_8 | uns_16 | 101 | Returns 0
Temperature sensor before stage 1.3 cooler | N | J | N | J | 14D0 | 14D1 | 2 | 14D0 | 2 | int_16 | int_32 | 104 | Returns 0
Error level | N | J | N | J | 14D8 | 14D8 | 1 | 14D8 | 1 | uns_8 | uns_16 | 108 | Returns 0
Temperature sensor before stage 1.4 cooler | N | J | N | J | 14DE | 14DF | 2 | 14DE | 2 | int_16 | int_32 | 111 | Returns 0
Error level | N | J | N | J | 14E6 | 14E6 | 1 | 14E6 |  | uns_8 | uns_16 | 115 | Returns 0
Temperature sensor before stage 1.5 cooler | N | J | N | J | 14EC | 14ED | 2 | 14EC | 2 | int_16 | int_32 | 118 | Returns 0
Error level | N | J | N | J | 14F4 | 14F4 | 1 | 14F4 | 1 | uns_8 | uns_16 | 122 | Returns 0
Temperature sensor before stage 2.1 cooler | N | J | N | J | 14FA | 14FB | 2 | 14FA | 2 | int_16 | int_32 | 125 | 0 | TT211
Error level | N | J | N | J | 1502 | 1502 | 1 | 1502 | 1 | uns_8 | uns_16 | 129 | 4
Temperature sensor before stage 2.2 cooler | N | J | N | J | 1508 | 1509 | 2 | 1508 | 2 | int_16 | int_32 | 132 | Returns 0
Error level | N | J | N | J | 1510 | 1510 | 1 | 1510 | 1 | uns_8 | uns_16 | 136 | Returns 0
Temperature sensor before stage 2.3 cooler | N | J | N | J | 1516 | 1517 | 2 | 1516 | 2 | int_16 | int_32 | 139 | Returns 0
Error level | N | J | N | J | 151E | 151E | 1 | 151E | 1 | uns_8 | uns_16 | 143 | Returns 0
Temperature sensor before stage 3.1 cooler | N | J | N | J | 1524 | 1525 | 2 | 1524 | 2 | int_16 | int_32 | 146 | 21 | TT311
Error level | N | J | N | J | 152C | 152C | 1 | 152C | 1 | uns_8 | uns_16 | 150 | 25
Temperature sensor before stage 3.2 cooler | N | J | N | J | 1532 | 1533 | 2 | 1532 | 2 | int_16 | int_32 | 153 | Returns 0
Error level | N | J | N | J | 153A | 153A | 1 | 153A | 1 | uns_8 | uns_16 | 157 | Returns 0
Temperature sensor before stage 4 cooler | N | J | N | J | 1540 | 1541 | 2 | 1540 | 2 | int_16 | int_32 | 160 | 35 | TT411
Error level | N | J | N | J | 1548 | 1548 | 1 | 1548 | 1 | uns_8 | uns_16 | 164 | 39
Temperature sensor before stage 5 cooler | N | J | N | J | 154E | 154F | 2 | 154E | 2 | int_16 | int_32 | 167 | Reads ~3570 | TT511
Error level | N | J | N | J | 1556 | 1556 | 1 | 1556 | 1 | uns_8 | uns_16 | 171
Temperature sensor before stage 6 cooler | N | J | N | J | 155C | 155D | 2 | 155C | 2 | int_16 | int_32 | 174 | No answer
Error level | N | J | N | J | 1564 | 1564 | 1 | 1564 | 1 | uns_8 | uns_16 | 178 | No answer
Stage temperature after stage 1.1 cooler | N | J | N | J | 156A | 156B | 2 | 156A | 2 | int_16 | int_32 | 181 | Returns 0
Error level | N | J | N | J | 1572 | 1572 | 1 | 1572 | 1 | uns_8 | uns_16 | 185 | Returns 0
Stage temperature after stage 1.2 cooler | N | J | N | J | 1578 | 1579 | 2 | 1578 | 2 | int_16 | int_32 | 188 | Returns 0
Error level | N | J | N | J | 1580 | 1580 | 1 | 1580 | 1 | uns_8 | uns_16 | 192 | Returns 0
Stage temperature after stage 1.3 cooler | N | J | N | J | 1586 | 1587 | 2 | 1586 | 2 | int_16 | int_32 | 195 | Returns 0
Error level | N | J | N | J | 158E | 158E | 1 | 158E | 1 | uns_8 | uns_16 | 199 | Returns 0
Stage temperature after stage 1.4 cooler | N | J | N | J | 1594 | 1595 | 2 | 1594 | 2 | int_16 | int_32 | 202 | Returns 0
Stage temperature after stage 1.5 cooler | N | J | N | J | 15A2 | 15A3 | 2 | 15A2 | 2 | int_16 | int_32 | 209 | Returns 0
Error level | N | J | N | J | 15AA | 15AA | 1 | 15AA | 1 | uns_8 | uns_16 | 213 | Returns 0
Stage temperature after stage 2.1 cooler | J ??? | J | N | J | 15B0 | 15B1 | 2 | 15B0 | 2 | int_16 | int_32 | 216 | Returns 0
Error level | N | J | N | J | 15B8 | 15B8 | 1 | 15B8 | 1 | uns_8 | uns_16 | 220 | Returns 0
Stage temperature after stage 2.2 cooler | J | J | N | J | 15BE | 15BF | 2 | 15BE | 2 | int_16 | int_32 | 223 | Returns 0
Error level | N | J | N | J | 15C6 | 15C6 | 1 | 15C6 | 1 | uns_8 | uns_16 | 227 | Returns 0
Stage temperature after stage 2.3 cooler | J ??? | J | N | J | 15CC | 15CD | 2 | 15CC | 2 | int_16 | int_32 | 230 | Returns 0
Error level | N | J | N | J | 15D4 | 15D4 | 1 | 15D4 | 1 | uns_8 | uns_16 | 234 | Returns 0
Stage temperature after stage 3.1 cooler | J ??? | J | N | J | 15DA | 15DB | 2 | 15DA | 2 | int_16 | int_32 | 237 | Returns 0
Error level | N | J | N | J | 15E2 | 15E2 | 1 | 15E2 | 1 | uns_8 | uns_16 | 241 | Returns 0
Stage temperature after stage 3.2 cooler | J ??? | J | N | J | 15E8 | 15E9 | 2 | 15E8 | 2 | int_16 | int_32 | 244 | Returns 0
Error level | N | J | N | J | 15F0 | 15F0 | 1 | 15F0 | 1 | uns_8 | uns_16 | 248 | Returns 0
Stage temperature after stage 4 cooler | J ??? | J | N | J | 15F6 | 15F7 | 2 | 15F6 | 2 | int_16 | int_32 | 251 | Returns 0
Error level | N | J | N | J | 15FE | 15FE | 1 | 15FE | 1 | uns_8 | uns_16 | 255 | Returns 0
Stage temperature after stage 5 cooler | J ??? | J | N | J | 1604 | 1605 | 2 | 1604 | 2 | int_16 | int_32 | 258 | Returns 0
Error level | N | J | N | J | 160C | 160C | 1 | 160C | 1 | uns_8 | uns_16 | 262 | Returns 0
Stage temperature after stage 6 cooler | J ??? | J | N | J | 1612 | 1613 | 2 | 1612 | 2 | int_16 | int_32 | 265 | No answer
Error level | N | J | N | J | 161A | 161A | 1 | 161A | 1 | uns_8 | uns_16 | 269 | No answer
Gas outlet temperature | J ??? | J | N | J | 1620 | 1621 | 2 | 1620 | 2 | int_16 | int_32 | 272 | No answer
Error level | N | J | N | J | 1628 | 1628 | 1 | 1628 |  | uns_8 | uns_16 | 276 | No answer
Note on I19: Konrad Gajewski: Field was empty in the original document

## Other values 1800-19FF
Data conversion type is the actual memory required, data conversion type reserve is the memory to be reserved for this variable
Register Name | Write access by Sauer | Read access by Sauer | Write access by customer | Read access by customer | Register Start | Register Stop | Max. Register Lenght | Register Adress | Register Lenght | Data Conversion Type | Data Conversion Type reserve | Note
Motor current | N | J | N | J | 1800 | 1801 | 2 | 1800 | 2 | uns_16 | uns_32 | OK
Frequency | N | J | N | J | 1814 | 1815 | 2 | 1814 | 2 | uns_16 | uns_32 | Reads 5000
Error level | N | J | N | J | 1817 | 1817 | 1 | 1817 | 1 | uns_8 | uns_16 | Reads 0
Oil level | N | J | N | J | 1823 | 1824 | 2 | 1823 | 2 | uns_16 | uns_32 | Reads 0
Error level | N | J | N | J | 182F | 182F | 1 | 182F | 1 | uns_8 | uns_16 | Reads 0

## Digital inputs 1A00-1BFF
Data conversion type is the actual memory required, data conversion type reserve is the memory to be reserved for this variable
Register Name | Write access by Sauer | Read access by Sauer | Write access by customer | Read access by customer | Register Start | Register Stop | Max. Register Lenght | Register Adress | Register Lenght | Data Conversion Type | Data Conversion Type reserve | Note
Digital input 1 | N | J | N | J | 1A00 | 1A00 | 1 | 1A00 | 1 | bool_8 | bool_16 | No answer
Function | N | J | N | J | 1A01 | 1A02 | 2 | 1A01 | 2 | uns_16 | uns_32 | No answer
NC/NO | N | J | N | J | 1A03 | 1A03 | 1 | 1A03 | 1 | bool_8 | bool_16
Signal delay | N | J | N | J | 1A04 | 1A05 | 2 | 1A04 | 2 | uns_16 | uns_32
Trigger warning | N | J | N | J | 1A06 | 1A06 | 1 | 1A06 | 1 | bool_8 | bool_16
Trigger error | N | J | N | J | 1A07 | 1A07 | 1 | 1A07 | 1 | bool_8 | bool_16
Digital input 2 | N | J | N | J | 1A08 | 1A08 | 1 | 1A08 | 1 | bool_8 | bool_16 | No answer
Function | N | J | N | J | 1A09 | 1A0A | 2 | 1A09 | 2 | uns_16 | uns_32 | No answer
NC/NO | N | J | N | J | 1A0B | 1A0B | 1 | 1A0B | 1 | bool_8 | bool_16
Signal delay | N | J | N | J | 1A0C | 1A0D | 2 | 1A0C | 2 | uns_16 | uns_32
Trigger warning | N | J | N | J | 1A0E | 1A0E | 1 | 1A0E | 1 | bool_8 | bool_16
Trigger error | N | J | N | J | 1A0F | 1A0F | 1 | 1A0F | 1 | bool_8 | bool_16
Digital input 3 | N | J | N | J | 1A10 | 1A10 | 1 | 1A10 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1A11 | 1A12 | 2 | 1A11 | 2 | uns_16 | uns_32
NC/NO | N | J | N | J | 1A13 | 1A13 | 1 | 1A13 | 1 | bool_8 | bool_16
Signal delay | N | J | N | J | 1A14 | 1A15 | 2 | 1A14 | 2 | uns_16 | uns_32
Trigger warning | N | J | N | J | 1A16 | 1A16 | 1 | 1A16 | 1 | bool_8 | bool_16
Trigger error | N | J | N | J | 1A17 | 1A17 | 1 | 1A17 | 1 | bool_8 | bool_16
Digital input 4 | N | J | N | J | 1A18 | 1A18 | 1 | 1A18 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1A19 | 1A1A | 2 | 1A19 | 2 | uns_16 | uns_32
NC/NO | N | J | N | J | 1A1B | 1A1B | 1 | 1A1B | 1 | bool_8 | bool_16
Signal delay | N | J | N | J | 1A1C | 1A1D | 2 | 1A1C | 2 | uns_16 | uns_32
Trigger warning | N | J | N | J | 1A1E | 1A1E | 1 | 1A1E | 1 | bool_8 | bool_16
Trigger error | N | J | N | J | 1A1F | 1A1F | 1 | 1A1F | 1 | bool_8 | bool_16
Digital input 5 | N | J | N | J | 1A20 | 1A20 | 1 | 1A20 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1A21 | 1A22 | 2 | 1A21 | 2 | uns_16 | uns_32
NC/NO | N | J | N | J | 1A23 | 1A23 | 1 | 1A23 | 1 | bool_8 | bool_16
Signal delay | N | J | N | J | 1A24 | 1A25 | 2 | 1A24 | 2 | uns_16 | uns_32
Trigger warning | N | J | N | J | 1A26 | 1A26 | 1 | 1A26 | 1 | bool_8 | bool_16
Trigger error | N | J | N | J | 1A27 | 1A27 | 1 | 1A27 | 1 | bool_8 | bool_16
Digital input 6 | N | J | N | J | 1A28 | 1A28 | 1 | 1A28 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1A29 | 1A2A | 2 | 1A29 | 2 | uns_16 | uns_32
NC/NO | N | J | N | J | 1A2B | 1A2B | 1 | 1A2B | 1 | bool_8 | bool_16
Signal delay | N | J | N | J | 1A2C | 1A2D | 2 | 1A2C | 2 | uns_16 | uns_32
Trigger warning | N | J | N | J | 1A2E | 1A2E | 1 | 1A2E | 1 | bool_8 | bool_16
Trigger error | N | J | N | J | 1A2F | 1A2F | 1 | 1A2F | 1 | bool_8 | bool_16
Digital input 7 | N | J | N | J | 1A30 | 1A30 | 1 | 1A30 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1A31 | 1A32 | 2 | 1A31 | 2 | uns_16 | uns_32
NC/NO | N | J | N | J | 1A33 | 1A33 | 1 | 1A33 | 1 | bool_8 | bool_16
Signal delay | N | J | N | J | 1A34 | 1A35 | 2 | 1A34 | 2 | uns_16 | uns_32
Trigger warning | N | J | N | J | 1A36 | 1A36 | 1 | 1A36 | 1 | bool_8 | bool_16
Trigger error | N | J | N | J | 1A37 | 1A37 | 1 | 1A37 | 1 | bool_8 | bool_16
Digital input 8 | N | J | N | J | 1A38 | 1A38 | 1 | 1A38 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1A39 | 1A3A | 2 | 1A39 | 2 | uns_16 | uns_32
NC/NO | N | J | N | J | 1A3B | 1A3B | 1 | 1A3B | 1 | bool_8 | bool_16
Signal delay | N | J | N | J | 1A3C | 1A3D | 2 | 1A3C | 2 | uns_16 | uns_32
Trigger warning | N | J | N | J | 1A3E | 1A3E | 1 | 1A3E | 1 | bool_8 | bool_16
Trigger error | N | J | N | J | 1A3F | 1A3F | 1 | 1A3F | 1 | bool_8 | bool_16
Digital input 9 | N | J | N | J | 1A40 | 1A40 | 1 | 1A40 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1A41 | 1A42 | 2 | 1A41 | 2 | uns_16 | uns_32
NC/NO | N | J | N | J | 1A43 | 1A43 | 1 | 1A43 | 1 | bool_8 | bool_16
Signal delay | N | J | N | J | 1A44 | 1A45 | 2 | 1A44 | 2 | uns_16 | uns_32
Trigger warning | N | J | N | J | 1A46 | 1A46 | 1 | 1A46 | 1 | bool_8 | bool_16
Trigger error | N | J | N | J | 1A47 | 1A47 | 1 | 1A47 | 1 | bool_8 | bool_16
Digital input 10 | N | J | N | J | 1A48 | 1A48 | 1 | 1A48 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1A49 | 1A4A | 2 | 1A49 | 2 | uns_16 | uns_32
NC/NO | N | J | N | J | 1A4B | 1A4B | 1 | 1A4B | 1 | bool_8 | bool_16
Signal delay | N | J | N | J | 1A4C | 1A4D | 2 | 1A4C | 2 | uns_16 | uns_32
Trigger warning | N | J | N | J | 1A4E | 1A4E | 1 | 1A4E | 1 | bool_8 | bool_16
Trigger error | N | J | N | J | 1A4F | 1A4F | 1 | 1A4F | 1 | bool_8 | bool_16
Digital input 11 | N | J | N | J | 1A50 | 1A50 | 1 | 1A50 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1A51 | 1A52 | 2 | 1A51 | 2 | uns_16 | uns_32
NC/NO | N | J | N | J | 1A53 | 1A53 | 1 | 1A53 | 1 | bool_8 | bool_16
Signal delay | N | J | N | J | 1A54 | 1A55 | 2 | 1A54 | 2 | uns_16 | uns_32
Trigger warning | N | J | N | J | 1A56 | 1A56 | 1 | 1A56 | 1 | bool_8 | bool_16
Trigger error | N | J | N | J | 1A57 | 1A57 | 1 | 1A57 | 1 | bool_8 | bool_16
Digital input 12 | N | J | N | J | 1A58 | 1A58 | 1 | 1A58 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1A59 | 1A5A | 2 | 1A59 | 2 | uns_16 | uns_32
NC/NO | N | J | N | J | 1A5B | 1A5B | 1 | 1A5B | 1 | bool_8 | bool_16
Signal delay | N | J | N | J | 1A5C | 1A5D | 2 | 1A5C | 2 | uns_16 | uns_32
Trigger warning | N | J | N | J | 1A5E | 1A5E | 1 | 1A5E | 1 | bool_8 | bool_16
Trigger error | N | J | N | J | 1A5F | 1A5F | 1 | 1A5F | 1 | bool_8 | bool_16
Digital input 13 | N | J | N | J | 1A60 | 1A60 | 1 | 1A60 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1A61 | 1A62 | 2 | 1A61 | 2 | uns_16 | uns_32
NC/NO | N | J | N | J | 1A63 | 1A63 | 1 | 1A63 | 1 | bool_8 | bool_16
Signal delay | N | J | N | J | 1A64 | 1A65 | 2 | 1A64 | 2 | uns_16 | uns_32
Trigger warning | N | J | N | J | 1A66 | 1A66 | 1 | 1A66 | 1 | bool_8 | bool_16
Trigger error | N | J | N | J | 1A67 | 1A67 | 1 | 1A67 | 1 | bool_8 | bool_16
Digital input 14 | N | J | N | J | 1A68 | 1A68 | 1 | 1A68 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1A69 | 1A6A | 2 | 1A69 | 2 | uns_16 | uns_32
NC/NO | N | J | N | J | 1A6B | 1A6B | 1 | 1A6B | 1 | bool_8 | bool_16
Signal delay | N | J | N | J | 1A6C | 1A6D | 2 | 1A6C | 2 | uns_16 | uns_32
Trigger warning | N | J | N | J | 1A6E | 1A6E | 1 | 1A6E | 1 | bool_8 | bool_16
Trigger error | N | J | N | J | 1A6F | 1A6F | 1 | 1A6F | 1 | bool_8 | bool_16
Digital input 15 | N | J | N | J | 1A70 | 1A70 | 1 | 1A70 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1A71 | 1A72 | 2 | 1A71 | 2 | uns_16 | uns_32
NC/NO | N | J | N | J | 1A73 | 1A73 | 1 | 1A73 | 1 | bool_8 | bool_16
Signal delay | N | J | N | J | 1A74 | 1A75 | 2 | 1A74 | 2 | uns_16 | uns_32
Trigger warning | N | J | N | J | 1A76 | 1A76 | 1 | 1A76 | 1 | bool_8 | bool_16
Trigger error | N | J | N | J | 1A77 | 1A77 | 1 | 1A77 | 1 | bool_8 | bool_16
Digital input 16 | N | J | N | J | 1A78 | 1A78 | 1 | 1A78 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1A79 | 1A7A | 2 | 1A79 | 2 | uns_16 | uns_32
NC/NO | N | J | N | J | 1A7B | 1A7B | 1 | 1A7B | 1 | bool_8 | bool_16
Signal delay | N | J | N | J | 1A7C | 1A7D | 2 | 1A7C | 2 | uns_16 | uns_32
Trigger warning | N | J | N | J | 1A7E | 1A7E | 1 | 1A7E | 1 | bool_8 | bool_16
Trigger error | N | J | N | J | 1A7F | 1A7F | 1 | 1A7F | 1 | bool_8 | bool_16
Digital input 17 | N | J | N | J | 1A80 | 1A80 | 1 | 1A80 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1A81 | 1A82 | 2 | 1A81 | 2 | uns_16 | uns_32
NC/NO | N | J | N | J | 1A83 | 1A83 | 1 | 1A83 | 1 | bool_8 | bool_16
Signal delay | N | J | N | J | 1A84 | 1A85 | 2 | 1A84 | 2 | uns_16 | uns_32
Trigger warning | N | J | N | J | 1A86 | 1A86 | 1 | 1A86 | 1 | bool_8 | bool_16
Trigger error | N | J | N | J | 1A87 | 1A87 | 1 | 1A87 | 1 | bool_8 | bool_16
Digital input 18 | N | J | N | J | 1A88 | 1A88 | 1 | 1A88 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1A89 | 1A8A | 2 | 1A89 | 2 | uns_16 | uns_32
NC/NO | N | J | N | J | 1A8B | 1A8B | 1 | 1A8B | 1 | bool_8 | bool_16
Signal delay | N | J | N | J | 1A8C | 1A8D | 2 | 1A8C | 2 | uns_16 | uns_32
Trigger warning | N | J | N | J | 1A8E | 1A8E | 1 | 1A8E | 1 | bool_8 | bool_16
Trigger error | N | J | N | J | 1A8F | 1A8F | 1 | 1A8F | 1 | bool_8 | bool_16
Digital input 19 | N | J | N | J | 1A90 | 1A90 | 1 | 1A90 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1A91 | 1A92 | 2 | 1A91 | 2 | uns_16 | uns_32
NC/NO | N | J | N | J | 1A93 | 1A93 | 1 | 1A93 | 1 | bool_8 | bool_16
Signal delay | N | J | N | J | 1A94 | 1A95 | 2 | 1A94 | 2 | uns_16 | uns_32
Trigger warning | N | J | N | J | 1A96 | 1A96 | 1 | 1A96 | 1 | bool_8 | bool_16
Trigger error | N | J | N | J | 1A97 | 1A97 | 1 | 1A97 | 1 | bool_8 | bool_16
Digital input 20 | N | J | N | J | 1A98 | 1A98 | 1 | 1A98 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1A99 | 1A9A | 2 | 1A99 | 2 | uns_16 | uns_32
NC/NO | N | J | N | J | 1A9B | 1A9B | 1 | 1A9B | 1 | bool_8 | bool_16
Signal delay | N | J | N | J | 1A9C | 1A9D | 2 | 1A9C | 2 | uns_16 | uns_32
Trigger warning | N | J | N | J | 1A9E | 1A9E | 1 | 1A9E | 1 | bool_8 | bool_16
Trigger error | N | J | N | J | 1A9F | 1A9F | 1 | 1A9F | 1 | bool_8 | bool_16
Digital input 21 | N | J | N | J | 1AA0 | 1AA0 | 1 | 1AA0 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1AA1 | 1AA2 | 2 | 1AA1 | 2 | uns_16 | uns_32
NC/NO | N | J | N | J | 1AA3 | 1AA3 | 1 | 1AA3 | 1 | bool_8 | bool_16
Signal delay | N | J | N | J | 1AA4 | 1AA5 | 2 | 1AA4 | 2 | uns_16 | uns_32
Trigger warning | N | J | N | J | 1AA6 | 1AA6 | 1 | 1AA6 | 1 | bool_8 | bool_16
Trigger error | N | J | N | J | 1AA7 | 1AA7 | 1 | 1AA7 | 1 | bool_8 | bool_16
Digital input 22 | N | J | N | J | 1AA8 | 1AA8 | 1 | 1AA8 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1AA9 | 1AAA | 2 | 1AA9 | 2 | uns_16 | uns_32
NC/NO | N | J | N | J | 1AAB | 1AAB | 1 | 1AAB | 1 | bool_8 | bool_16
Signal delay | N | J | N | J | 1AAC | 1AAD | 2 | 1AAC | 2 | uns_16 | uns_32
Trigger warning | N | J | N | J | 1AAE | 1AAE | 1 | 1AAE | 1 | bool_8 | bool_16
Trigger error | N | J | N | J | 1AAF | 1AAF | 1 | 1AAF | 1 | bool_8 | bool_16
Digital input 23 | N | J | N | J | 1AB0 | 1AB0 | 1 | 1AB0 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1AB1 | 1AB2 | 2 | 1AB1 | 2 | uns_16 | uns_32
NC/NO | N | J | N | J | 1AB3 | 1AB3 | 1 | 1AB3 | 1 | bool_8 | bool_16
Signal delay | N | J | N | J | 1AB4 | 1AB5 | 2 | 1AB4 | 2 | uns_16 | uns_32
Trigger warning | N | J | N | J | 1AB6 | 1AB6 | 1 | 1AB6 | 1 | bool_8 | bool_16
Trigger error | N | J | N | J | 1AB7 | 1AB7 | 1 | 1AB7 | 1 | bool_8 | bool_16
Digital input 24 | N | J | N | J | 1AB8 | 1AB8 | 1 | 1AB8 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1AB9 | 1ABA | 2 | 1AB9 | 2 | uns_16 | uns_32
NC/NO | N | J | N | J | 1ABB | 1ABB | 1 | 1ABB | 1 | bool_8 | bool_16
Signal delay | N | J | N | J | 1ABC | 1ABD | 2 | 1ABC | 2 | uns_16 | uns_32
Trigger warning | N | J | N | J | 1ABE | 1ABE | 1 | 1ABE | 1 | bool_8 | bool_16
Trigger error | N | J | N | J | 1ABF | 1ABF | 1 | 1ABF | 1 | bool_8 | bool_16

## Digital outputs 1C00-1DFF
Data conversion type is the actual memory required, data conversion type reserve is the memory to be reserved for this variable
Register Name | Write access by Sauer | Read access by Sauer | Write access by customer | Read access by customer | Register Start | Register Stop | Max. Register Lenght | Register Adress | Register Lenght | Data Conversion Type | Data Conversion Type reserve | Note
Digital output 1 | N | J | N | J | 1C00 | 1C00 | 1 | 1C00 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1C01 | 1C02 | 2 | 1C01 | 2 | uns_16 | uns_32
Switching delay | N | J | N | J | 1C03 | 1C04 | 2 | 1C03 | 2 | uns_16 | uns_32
Digital output 2 | N | J | N | J | 1C05 | 1C05 | 1 | 1C05 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1C06 | 1C07 | 2 | 1C06 | 2 | uns_16 | uns_32
Switching delay | N | J | N | J | 1C08 | 1C09 | 2 | 1C08 | 2 | uns_16 | uns_32
Digital output 3 | N | J | N | J | 1C0A | 1C0A | 1 | 1C0A | 1 | bool_8 | bool_16
Function | N | J | N | J | 1C0B | 1C0C | 2 | 1C0B | 2 | uns_16 | uns_32
Switching delay | N | J | N | J | 1C0D | 1C0E | 2 | 1C0D | 2 | uns_16 | uns_32
Digital output 4 | N | J | N | J | 1C0F | 1C0F | 1 | 1C0F | 1 | bool_8 | bool_16
Function | N | J | N | J | 1C10 | 1C11 | 2 | 1C10 | 2 | uns_16 | uns_32
Switching delay | N | J | N | J | 1C12 | 1C13 | 2 | 1C12 | 2 | uns_16 | uns_32
Digital output 5 | N | J | N | J | 1C14 | 1C14 | 1 | 1C14 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1C15 | 1C16 | 2 | 1C15 | 2 | uns_16 | uns_32
Switching delay | N | J | N | J | 1C17 | 1C18 | 2 | 1C17 | 2 | uns_16 | uns_32
Digital output 6 | N | J | N | J | 1C19 | 1C19 | 1 | 1C19 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1C1A | 1C1B | 2 | 1C1A | 2 | uns_16 | uns_32
Switching delay | N | J | N | J | 1C1C | 1C1D | 2 | 1C1C | 2 | uns_16 | uns_32
Digital output 7 | N | J | N | J | 1C1E | 1C1E | 1 | 1C1E | 1 | bool_8 | bool_16 | No answer
Function | N | J | N | J | 1C1F | 1C20 | 2 | 1C1F | 2 | uns_16 | uns_32 | No answer
Switching delay | N | J | N | J | 1C21 | 1C22 | 2 | 1C21 | 2 | uns_16 | uns_32 | No answer
Digital output 8 | N | J | N | J | 1C23 | 1C23 | 1 | 1C23 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1C24 | 1C25 | 2 | 1C24 | 2 | uns_16 | uns_32
Switching delay | N | J | N | J | 1C26 | 1C27 | 2 | 1C26 | 2 | uns_16 | uns_32
Digital output 9 | N | J | N | J | 1C28 | 1C28 | 1 | 1C28 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1C29 | 1C2A | 2 | 1C29 | 2 | uns_16 | uns_32
Switching delay | N | J | N | J | 1C2B | 1C2C | 2 | 1C2B | 2 | uns_16 | uns_32
Digital output 10 | N | J | N | J | 1C2D | 1C2D | 1 | 1C2D | 1 | bool_8 | bool_16
Function | N | J | N | J | 1C2E | 1C2F | 2 | 1C2E | 2 | uns_16 | uns_32
Switching delay | N | J | N | J | 1C30 | 1C31 | 2 | 1C30 | 2 | uns_16 | uns_32
Digital output 11 | N | J | N | J | 1C32 | 1C32 | 1 | 1C32 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1C33 | 1C34 | 2 | 1C33 | 2 | uns_16 | uns_32
Switching delay | N | J | N | J | 1C35 | 1C36 | 2 | 1C35 | 2 | uns_16 | uns_32
Digital output 12 | N | J | N | J | 1C37 | 1C37 | 1 | 1C37 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1C38 | 1C39 | 2 | 1C38 | 2 | uns_16 | uns_32
Switching delay | N | J | N | J | 1C3A | 1C3B | 2 | 1C3A | 2 | uns_16 | uns_32
Digital output 13 | N | J | N | J | 1C3C | 1C3C | 1 | 1C3C | 1 | bool_8 | bool_16
Function | N | J | N | J | 1C3D | 1C3E | 2 | 1C3D | 2 | uns_16 | uns_32
Switching delay | N | J | N | J | 1C3F | 1C40 | 2 | 1C3F | 2 | uns_16 | uns_32
Digital output 14 | N | J | N | J | 1C41 | 1C41 | 1 | 1C41 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1C42 | 1C43 | 2 | 1C42 | 2 | uns_16 | uns_32
Switching delay | N | J | N | J | 1C44 | 1C45 | 2 | 1C44 | 2 | uns_16 | uns_32
Digital output 15 | N | J | N | J | 1C46 | 1C46 | 1 | 1C46 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1C47 | 1C48 | 2 | 1C47 | 2 | uns_16 | uns_32
Switching delay | N | J | N | J | 1C49 | 1C4A | 2 | 1C49 | 2 | uns_16 | uns_32
Digital output 16 | N | J | N | J | 1C4B | 1C4B | 1 | 1C4B | 1 | bool_8 | bool_16
Function | N | J | N | J | 1C4C | 1C4D | 2 | 1C4C | 2 | uns_16 | uns_32
Switching delay | N | J | N | J | 1C4E | 1C4F | 2 | 1C4E | 2 | uns_16 | uns_32
Digital output 17 | N | J | N | J | 1C50 | 1C50 | 1 | 1C50 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1C51 | 1C52 | 2 | 1C51 | 2 | uns_16 | uns_32
Switching delay | N | J | N | J | 1C53 | 1C54 | 2 | 1C53 | 2 | uns_16 | uns_32
Digital output 18 | N | J | N | J | 1C55 | 1C55 | 1 | 1C55 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1C56 | 1C57 | 2 | 1C56 | 2 | uns_16 | uns_32
Switching delay | N | J | N | J | 1C58 | 1C59 | 2 | 1C58 | 2 | uns_16 | uns_32
Digital output 19 | N | J | N | J | 1C5A | 1C5A | 1 | 1C5A | 1 | bool_8 | bool_16
Function | N | J | N | J | 1C5B | 1C5C | 2 | 1C5B | 2 | uns_16 | uns_32
Switching delay | N | J | N | J | 1C5D | 1C5E | 2 | 1C5D | 2 | uns_16 | uns_32
Digital output 20 | N | J | N | J | 1C5F | 1C5F | 1 | 1C5F | 1 | bool_8 | bool_16
Function | N | J | N | J | 1C60 | 1C61 | 2 | 1C60 | 2 | uns_16 | uns_32
Switching delay | N | J | N | J | 1C62 | 1C63 | 2 | 1C62 | 2 | uns_16 | uns_32
Digital output 21 | N | J | N | J | 1C64 | 1C64 | 1 | 1C64 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1C65 | 1C66 | 2 | 1C65 | 2 | uns_16 | uns_32
Switching delay | N | J | N | J | 1C67 | 1C68 | 2 | 1C67 | 2 | uns_16 | uns_32
Digital output 22 | N | J | N | J | 1C69 | 1C69 | 1 | 1C69 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1C6A | 1C6B | 2 | 1C6A | 2 | uns_16 | uns_32
Switching delay | N | J | N | J | 1C6C | 1C6D | 2 | 1C6C | 2 | uns_16 | uns_32
Digital output 23 | N | J | N | J | 1C6E | 1C6E | 1 | 1C6E | 1 | bool_8 | bool_16
Function | N | J | N | J | 1C6F | 1C70 | 2 | 1C6F | 2 | uns_16 | uns_32
Switching delay | N | J | N | J | 1C71 | 1C72 | 2 | 1C71 | 2 | uns_16 | uns_32
Digital output 24 | N | J | N | J | 1C73 | 1C73 | 1 | 1C73 | 1 | bool_8 | bool_16
Function | N | J | N | J | 1C74 | 1C75 | 2 | 1C74 | 2 | uns_16 | uns_32
Switching delay | N | J | N | J | 1C76 | 1C77 | 2 | 1C76 | 2 | uns_16 | uns_32

## Analog inputs 1E00-1FFF
Data conversion type is the actual memory required, data conversion type reserve is the memory to be reserved for this variable
Register Name | Write access by Sauer | Read access by Sauer | Write access by customer | Read access by customer | Register Start | Register Stop | Max. Register Lenght | Register Adress | Register Lenght | Data Conversion Type | Data Conversion Type reserve | Notes
Analog input 1 | N | J | N | J | 1E00 | 1E01 | 2 | 1E00 | 2 | uns_16 | uns_32 | No answer
Analog input 2 | N | J | N | J | 1E0A | 1E0B | 2 | 1E0A | 2 | uns_16 | uns_32 | No answer
Analog input 3 | N | J | N | J | 1E14 | 1E15 | 2 | 1E14 | 2 | uns_16 | uns_32 | No answer
Analog input 4 | N | J | N | J | 1E1E | 1E1F | 2 | 1E1E | 2 | uns_16 | uns_32 | No answer
Analog input 5 | N | J | N | J | 1E28 | 1E29 | 2 | 1E28 | 2 | uns_16 | uns_32 | No answer
Analog input 6 | N | J | N | J | 1E32 | 1E33 | 2 | 1E32 | 2 | uns_16 | uns_32 | No answer
Analog input 7 | N | J | N | J | 1E3C | 1E3D | 2 | 1E3C | 2 | uns_16 | uns_32 | No answer
Analog input 8 | N | J | N | J | 1E46 | 1E47 | 2 | 1E46 | 2 | uns_16 | uns_32
Analog input 9 | N | J | N | J | 1E50 | 1E51 | 2 | 1E50 | 2 | uns_16 | uns_32 | No answer
Analog input 10 | N | J | N | J | 1E5A | 1E5B | 2 | 1E5A | 2 | uns_16 | uns_32 | No answer
Analog input 11 | N | J | N | J | 1E64 | 1E65 | 2 | 1E64 | 2 | uns_16 | uns_32 | No answer
Analog input 12 | N | J | N | J | 1E6E | 1E6F | 2 | 1E6E | 2 | uns_16 | uns_32 | No answer
Analog input 13 | N | J | N | J | 1E78 | 1E79 | 2 | 1E78 | 2 | uns_16 | uns_32
Analog input 14 | N | J | N | J | 1E82 | 1E83 | 2 | 1E82 | 2 | uns_16 | uns_32
Analog input 15 | N | J | N | J | 1E8C | 1E8D | 2 | 1E8C | 2 | uns_16 | uns_32
Analog input 16 | N | J | N | J | 1E96 | 1E97 | 2 | 1E96 | 2 | uns_16 | uns_32
Analog input 17 | N | J | N | J | 1EA0 | 1EA1 | 2 | 1EA0 | 2 | uns_16 | uns_32
Analog input 18 | N | J | N | J | 1EAA | 1EAB | 2 | 1EAA | 2 | uns_16 | uns_32
Analog input 19 | N | J | N | J | 1EB4 | 1EB5 | 2 | 1EB4 | 2 | uns_16 | uns_32
Analog input 20 | N | J | N | J | 1EBE | 1EBF | 2 | 1EBE | 2 | uns_16 | uns_32
Analog input 21 | N | J | N | J | 1EC8 | 1EC9 | 2 | 1EC8 | 2 | uns_16 | uns_32
Analog input 22 | N | J | N | J | 1ED2 | 1ED3 | 2 | 1ED2 | 2 | uns_16 | uns_32
Analog input 23 | N | J | N | J | 1EDC | 1EDD | 2 | 1EDC | 2 | uns_16 | uns_32
Analog input 24 | N | J | N | J | 1EE6 | 1EE7 | 2 | 1EE6 | 2 | uns_16 | uns_32
Analog input 25 | N | J | N | J | 1EF0 | 1EF1 | 2 | 1EF0 | 2 | uns_16 | uns_32
Analog input 26 | N | J | N | J | 1EFA | 1EFB | 2 | 1EFA | 2 | uns_16 | uns_32
Analog input 27 | N | J | N | J | 1F04 | 1F05 | 2 | 1F04 | 2 | uns_16 | uns_32 | No answer
Analog input 28 | N | J | N | J | 1F0E | 1F0F | 2 | 1F0E | 2 | uns_16 | uns_32
Analog input 29 | N | J | N | J | 1F18 | 1F19 | 2 | 1F18 | 2 | uns_16 | uns_32
Analog input 30 | N | J | N | J | 1F22 | 1F23 | 2 | 1F22 | 2 | uns_16 | uns_32

## Reserve 2200-23FF
Dateityp Bool 1 Register |  |  |  | Bis kw 46
Data conversion type is the actual memory required, data conversion type reserve is the memory to be reserved for this variable
Alle anderen Dateitypen 2 Register
| Register Name | Schreibzugriff von Sauer | Lesezugriff von Sauer | Schreibzugriff vom Kunden | Lesezugriff vom Kunden | Register Start | Register Stop | Max. Register Lenght | Register Adress | Register Lenght | Data Conversion Type | Data Conversion Type reserve | Note
| Hrs until maintenance | N | J | N | J | 2200 | 2201 | 2 | 2200 | 2 | int_32 | int_32 | No answer
| Start | J | J | J | J | 2206 | 2207 | 2 | 2206 | 2 | uns_16 | uns_16 | No answer
| stop | J | J | J | J | 2208 | 2209 | 2 | 2208 | 2 | uns_16 | uns_16 | No answer

## Modes and menue 2400-25FF
Data conversion type is the actual memory required, data conversion type reserve is the memory to be reserved for this variable
Register Name | Write access by Sauer | Read access by Sauer | Write access by customer | Read access by customer | Register Start | Register Stop | Max. Register Lenght | Register Adress | Register Lenght | Data Conversion Type | Data Conversion Type reserve | Note
Operating mode | J | J | J | J | 2400 | 2400 | 1 | 2400 | 1 | bool_8 | bool_16 | 0x7e01 when running
Remote start Status | J | J | J | J | 2401 | 2401 | 1 | 2401 | 1 | bool_8 | bool_16 | 0x7e01 when running
Remote start by pilot | J | J | J | J | 2402 | 2402 | 1 | 2402 | 1 | bool_8 | bool_16 | 0x7e00 when running
Hysteresis | J | J | J | J | 2403 | 2404 | 2 | 2403 | 2 | uns_16 | uns_32 | 1000 when running
Default settings Language | J | J | J | J | 2468 | 2468 | 1 | 2468 | 1 | uns_8 | uns_16 | Changes between 0 and 0x7e00
Time Hour | J | J | J | J | 2469 | 2469 | 1 | 2469 | 1 | uns_8 | uns_16 | LSByte reads 0, MSB changes 0x25/0x7e
Minute | J | J | J | J | 246A | 246A | 1 | 246A | 1 | uns_8 | uns_16 | LSByte reads 0, MSB changes 0x25/0x7e
Time format | J | J | J | J | 246B | 246B | 1 | 246B | 1 | bool_8 | bool_16 | LSByte reads 1, MSB changes 0x25/0x7e
Date Day | J | J | J | J | 246C | 246C | 1 | 246C | 1 | uns_8 | uns_16 | LSByte reads 0, MSB changes 0x25/0x7e
Month | J | J | J | J | 246D | 246D | 1 | 246D | 1 | uns_8 | uns_16 | LSByte reads 0, MSB changes 0x25/0x7e
Year | J | J | J | J | 246E | 246F | 1 | 246E | 2 | uns_16 | uns_32 | Reads 0
Date format | J | J | J | J | 2470 | 2470 | 1 | 2470 | 1 | uns_8 | uns_16 | LSByte reads 0, MSB changes 0x25/0x7e
Network settings Ethernet DhcpActive | J | J | J | J | 2479 | 2479 | 1 | 2479 | 1 | bool_8 | bool_16 | LSByte reads 0, MSB changes 0x25/0x7e
IP address | J | J | J | J | 247A | 2489 | 16 | 247A | 16 | text[16] | text[32]
Net mask | J | J | J | J | 248A | 2499 | 16 | 248A | 16 | text[16] | text[32]
Gateway | J | J | J | J | 249A | 24A9 | 16 | 249A | 16 | text[16] | text[32]
StartUdpIoThread | J | J | J | J | 24AA | 24AA | 1 | 24AA | 1 | bool_8 | bool_16 | No answer
RS485 Bus type | J | J | J | J | 24AB | 24AC | 2 | 24AB | 2 | enum / uns_32 | enum uns_32 | Switches between 0, 1, 9 ????
Bus address | J | J | J | J | 24AD | 24AD | 1 | 24AD | 1 | uns_8 | uns_16 | Changes between 0x7e02 and 0x2502
Baud rate | J | J | J | J | 24AE | 24AF | 2 | 24AE | 2 | enum / uns_32 | enum uns_32 | Reads 9600
Parity | J | J | J | J | 24B0 | 24B0 | 1 | 24B0 | 1 | uns_8 | uns_16 | Reads 0
Data bits | J | J | J | J | 24B1 | 24B1 | 1 | 24B1 | 1 | uns_8 | uns_16 | Reads 8
End bits | J | J | J | J | 24B2 | 24B2 | 1 | 24B2 | 1 | uns_8 | uns_16 | Reads 1
RS232 Bus type | J | J | J | J | 24B3 | 24B4 | 2 | 24B3 | 2 | enum / uns_32 | enum / uns_32 | Switches between 0x50, 1, 9 ????
Bus address | J | J | J | J | 24B5 | 24B5 | 1 | 24B5 | 1 | uns_8 | uns_16 | Reads 0
Baud rate | J | J | J | J | 24B6 | 24B7 | 2 | 24B6 | 2 | enum / uns_32 | enum / uns_32 | Reads 19200
Parity | J | J | J | J | 24B8 | 24B8 | 1 | 24B8 | 1 | uns_8 | uns_16 | Reads 0
Data bits | J | J | J | J | 24B9 | 24B9 | 1 | 24B9 | 1 | uns_8 | uns_16 | Reads 8
End bits | J | J | J | J | 24BA | 24BA | 1 | 24BA | 1 | uns_8 | uns_16 | Reads 1

## Timer,DisplayService 2600-27FF
Data conversion type is the actual memory required, data conversion type reserve is the memory to be reserved for this variable
Register Name | Write access by Sauer | Read access by Sauer | Write access by customer | Read access by customer | Register Start | Register Stop | Max. Register Lenght | Register Adress | Register Lenght | Data Conversion Type | Data Conversion Type reserve | Note
Automatic black start | J | J | J | J | 2604 | 2605 | 2 | 2604 | 2 | uns_16 | uns_32 | Reads 5000
Kompressorstatus | J | J | N | J | 2623 | 2623 | 1 | 2623 | 1 | enum / uns_8 | enum / uns_16 | OK
[6 empty] | German | English
|  |  |  | Kompressorstatus | Dezimal | Bedeutung
[5 empty] | 0 | Fehler | Error
[5 empty] | 1 | Initialisierung | Initialization
[5 empty] | 2 | Startbehinderung | start inhibit
[5 empty] | 3 | Startbereit | Ready to start
[5 empty] | 4 | Betriebsbehinderung | Obstruction of operation
[5 empty] | 5 | Standby | Standby
[5 empty] | 6 | Anlaufentlastung | Start-up relief
[5 empty] | 7 | Startet | Starts
[5 empty] | 8 | Belastungsverzögerung | Load delay
[5 empty] | 9 | Belastet | Running
[5 empty] | 10 | Wiederbelastungsverzögerung | Reload Delay
[5 empty] | 11 | Offload | Offload
[5 empty] | 12 | Gestoppt | Stopped
[5 empty] | 13 | Entwässerung | Drainage